## bus
| name | vn_kv | type | zone | in_service | max_vm_pu | min_vm_pu
0 | 1 | 345 | b | 1 | TRUE | 1.1 | 0.9
1 | 2 | 345 | b | 1 | TRUE | 1.1 | 0.9
2 | 3 | 345 | b | 1 | TRUE | 1.1 | 0.9
3 | 4 | 345 | b | 1 | TRUE | 1.1 | 0.9
4 | 5 | 345 | b | 1 | TRUE | 1.1 | 0.9
5 | 6 | 345 | b | 1 | TRUE | 1.1 | 0.9
6 | 7 | 345 | b | 1 | TRUE | 1.1 | 0.9
7 | 8 | 345 | b | 1 | TRUE | 1.1 | 0.9
8 | 9 | 345 | b | 1 | TRUE | 1.1 | 0.9

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type | controllable
0 |  | 4 | 90 | 30 | 0 | 0 |  | 1 | TRUE |  | FALSE
1 |  | 6 | 100 | 35 | 0 | 0 |  | 1 | TRUE |  | FALSE
2 |  | 8 | 125 | 50 | 0 | 0 |  | 1 | TRUE |  | FALSE

## gen
| name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | in_service | slack_weight | type | controllable | max_p_mw | min_p_mw
0 |  | 1 | 163 | 1 |  | -300 | 300 | 1 | FALSE | TRUE | 0 |  | TRUE | 300 | 10
1 |  | 2 | 85 | 1 |  | -300 | 300 | 1 | FALSE | TRUE | 0 |  | TRUE | 270 | 10

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | max_p_mw | min_p_mw | max_q_mvar | min_q_mvar
0 |  | 0 | 1 | 0 | 1 | TRUE | 250 | 10 | 300 | -300

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | max_loading_percent
0 |  |  | 0 | 3 | 1 | 0 | 68.5584 | 0 | 0 | 0.41837 | 1 | 1 | ol | TRUE | 100
1 |  |  | 3 | 4 | 1 | 20.2342 | 109.503 | 352.1176 | 0 | 0.41837 | 1 | 1 | ol | TRUE | 100
2 |  |  | 4 | 5 | 1 | 46.4198 | 202.3425 | 797.8362 | 0 | 0.25102 | 1 | 1 | ol | TRUE | 100
3 |  |  | 2 | 5 | 1 | 0 | 69.7486 | 0 | 0 | 0.50204 | 1 | 1 | ol | TRUE | 100
4 |  |  | 5 | 6 | 1 | 14.164 | 119.9772 | 465.7759 | 0 | 0.25102 | 1 | 1 | ol | TRUE | 100
5 |  |  | 6 | 7 | 1 | 10.1171 | 85.698 | 332.0603 | 0 | 0.41837 | 1 | 1 | ol | TRUE | 100
6 |  |  | 7 | 1 | 1 | 0 | 74.3906 | 0 | 0 | 0.41837 | 1 | 1 | ol | TRUE | 100
7 |  |  | 7 | 8 | 1 | 38.088 | 191.6302 | 681.9493 | 0 | 0.41837 | 1 | 1 | ol | TRUE | 100
8 |  |  | 8 | 3 | 1 | 11.9025 | 101.1713 | 392.2323 | 0 | 0.41837 | 1 | 1 | ol | TRUE | 100

## poly_cost
| element | et | cp0_eur | cp1_eur_per_mw | cp2_eur_per_mw2 | cq0_eur | cq1_eur_per_mvar | cq2_eur_per_mvar2
0 | 0 | ext_grid | 150 | 5 | 0.11 | 0 | 0 | 0
1 | 0 | gen | 600 | 1.2 | 0.085 | 0 | 0 | 0
2 | 1 | gen | 335 | 1 | 0.1225 | 0 | 0 | 0

## bus_geodata
| x | y | coords
0 | -2.9134 | -0.64388
1 | 0.93699 | -0.11737
2 | -1.4518 | 2.9406
3 | -2.0549 | 0.0097927
4 | -2.1789 | 1.1489
5 | -1.2944 | 1.8719
6 | -0.2435 | 1.4166
7 | -0.063903 | 0.28582
8 | -0.98302 | -0.39409

## line_std_types
| c_nf_per_km | max_i_ka | q_mm2 | r_ohm_per_km | type | x_ohm_per_km
122-AL1/20-ST1A 10.0 | 11.1 | 0.41 | 122 | 0.2376 | ol | 0.323
122-AL1/20-ST1A 20.0 | 10.3 | 0.41 | 122 | 0.2376 | ol | 0.344
149-AL1/24-ST1A 10.0 | 11.25 | 0.47 | 149 | 0.194 | ol | 0.315
149-AL1/24-ST1A 110.0 | 8.75 | 0.47 | 149 | 0.194 | ol | 0.41
149-AL1/24-ST1A 20.0 | 10.5 | 0.47 | 149 | 0.194 | ol | 0.337
15-AL1/3-ST1A 0.4 | 11 | 0.105 | 16 | 1.8769 | ol | 0.35
184-AL1/30-ST1A 110.0 | 8.8 | 0.535 | 184 | 0.1571 | ol | 0.4
184-AL1/30-ST1A 20.0 | 10.75 | 0.535 | 184 | 0.1571 | ol | 0.33
24-AL1/4-ST1A 0.4 | 11.25 | 0.14 | 24 | 1.2012 | ol | 0.335
243-AL1/39-ST1A 110.0 | 9 | 0.645 | 243 | 0.1188 | ol | 0.39
243-AL1/39-ST1A 20.0 | 11 | 0.645 | 243 | 0.1188 | ol | 0.32
305-AL1/39-ST1A 110.0 | 9.2 | 0.74 | 305 | 0.0949 | ol | 0.38
34-AL1/6-ST1A 10.0 | 9.7 | 0.17 | 34 | 0.8342 | ol | 0.36
34-AL1/6-ST1A 20.0 | 9.15 | 0.17 | 34 | 0.8342 | ol | 0.382
48-AL1/8-ST1A 0.4 | 12.2 | 0.21 | 48 | 0.5939 | ol | 0.3
48-AL1/8-ST1A 10.0 | 10.1 | 0.21 | 48 | 0.5939 | ol | 0.35
48-AL1/8-ST1A 20.0 | 9.5 | 0.21 | 48 | 0.5939 | ol | 0.372
490-AL1/64-ST1A 220.0 | 10 | 0.96 | 490 | 0.059 | ol | 0.285
490-AL1/64-ST1A 380.0 | 11 | 0.96 | 490 | 0.059 | ol | 0.253
70-AL1/11-ST1A 10.0 | 10.4 | 0.29 | 70 | 0.4132 | ol | 0.339
70-AL1/11-ST1A 20.0 | 9.7 | 0.29 | 70 | 0.4132 | ol | 0.36
94-AL1/15-ST1A 0.4 | 13.2 | 0.35 | 94 | 0.306 | ol | 0.29
94-AL1/15-ST1A 10.0 | 10.75 | 0.35 | 94 | 0.306 | ol | 0.33
94-AL1/15-ST1A 20.0 | 10 | 0.35 | 94 | 0.306 | ol | 0.35
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.366 | 120 | 0.153 | cs | 0.166
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.457 | 185 | 0.099 | cs | 0.156
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.526 | 240 | 0.075 | cs | 0.149
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.588 | 300 | 0.06 | cs | 0.144
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.283 | 120 | 0.253 | cs | 0.119
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.28 | 120 | 0.253 | cs | 0.113
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.319 | 150 | 0.206 | cs | 0.116
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.315 | 150 | 0.206 | cs | 0.11
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.362 | 185 | 0.161 | cs | 0.117
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.358 | 185 | 0.161 | cs | 0.11
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.421 | 240 | 0.122 | cs | 0.112
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.416 | 240 | 0.122 | cs | 0.105
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.22 | 70 | 0.443 | cs | 0.132
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.217 | 70 | 0.443 | cs | 0.123
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.252 | 95 | 0.313 | cs | 0.132
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.249 | 95 | 0.313 | cs | 0.123
NAYY 4x120 SE | 264 | 0.242 | 120 | 0.225 | cs | 0.08
NAYY 4x150 SE | 261 | 0.27 | 150 | 0.208 | cs | 0.08
NAYY 4x50 SE | 210 | 0.142 | 50 | 0.642 | cs | 0.083

## trafo_std_types
| i0_percent | pfe_kw | shift_degree | vector_group | vn_hv_kv | vn_lv_kv | sn_mva | tap_max | tap_neutral | tap_min | tap_phase_shifter | tap_side | tap_step_degree | tap_step_percent | vk_percent | vkr_percent
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 150 | Dyn5 | 10 | 0.4 | 0.25 | 2 | 0 | -2 | FALSE | hv | 0 | 2.5 | 4 | 1.2
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 150 | Yzn5 | 20 | 0.4 | 0.25 | 2 | 0 | -2 | FALSE | hv | 0 | 2.5 | 6 | 1.44
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 150 | Dyn5 | 10 | 0.4 | 0.4 | 2 | 0 | -2 | FALSE | hv | 0 | 2.5 | 4 | 1.325
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 150 | Dyn5 | 20 | 0.4 | 0.4 | 2 | 0 | -2 | FALSE | hv | 0 | 2.5 | 6 | 1.425
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 150 | Dyn5 | 10 | 0.4 | 0.63 | 2 | 0 | -2 | FALSE | hv | 0 | 2.5 | 4 | 1.0794
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 150 | Dyn5 | 20 | 0.4 | 0.63 | 2 | 0 | -2 | FALSE | hv | 0 | 2.5 | 6 | 1.206
100 MVA 220/110 kV | 0.06 | 55 | 0 | Yy0 | 220 | 110 | 100 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 12 | 0.26
160 MVA 380/110 kV | 0.06 | 60 | 0 | Yy0 | 380 | 110 | 160 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 12.2 | 0.25
25 MVA 110/10 kV | 0.07 | 14 | 150 | YNd5 | 110 | 10 | 25 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 12 | 0.41
25 MVA 110/10 kV v1.4.3 and older | 0.073 | 28.51 | 150 | YNd5 | 110 | 10 | 25 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 10.04 | 0.276
25 MVA 110/20 kV | 0.07 | 14 | 150 | YNd5 | 110 | 20 | 25 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 12 | 0.41
25 MVA 110/20 kV v1.4.3 and older | 0.071 | 29 | 150 | YNd5 | 110 | 20 | 25 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 11.2 | 0.282
40 MVA 110/10 kV | 0.05 | 18 | 150 | YNd5 | 110 | 10 | 40 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 16.2 | 0.34
40 MVA 110/10 kV v1.4.3 and older | 0.076 | 30.45 | 150 | YNd5 | 110 | 10 | 40 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 10.04 | 0.295
40 MVA 110/20 kV | 0.05 | 18 | 150 | YNd5 | 110 | 20 | 40 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 16.2 | 0.34
40 MVA 110/20 kV v1.4.3 and older | 0.08 | 31 | 150 | YNd5 | 110 | 20 | 40 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 11.2 | 0.302
63 MVA 110/10 kV | 0.04 | 22 | 150 | YNd5 | 110 | 10 | 63 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 18 | 0.32
63 MVA 110/10 kV v1.4.3 and older | 0.078 | 31.51 | 150 | YNd5 | 110 | 10 | 63 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 10.04 | 0.31
63 MVA 110/20 kV | 0.04 | 22 | 150 | YNd5 | 110 | 20 | 63 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 18 | 0.32
63 MVA 110/20 kV v1.4.3 and older | 0.086 | 33 | 150 | YNd5 | 110 | 20 | 63 | 9 | 0 | -9 | FALSE | hv | 0 | 1.5 | 11.2 | 0.322

## trafo3w_std_types
| i0_percent | pfe_kw | shift_lv_degree | shift_mv_degree | vector_group | vn_hv_kv | vn_lv_kv | vn_mv_kv | sn_hv_mva | sn_lv_mva | sn_mv_mva | tap_max | tap_neutral | tap_min | tap_side | tap_step_percent | vk_hv_percent | vk_lv_percent | vk_mv_percent | vkr_hv_percent | vkr_lv_percent | vkr_mv_percent
63/25/38 MVA 110/10/10 kV | 0.89 | 35 | 0 | 0 | YN0yn0yn0 | 110 | 10 | 10 | 63 | 38 | 25 | 10 | 0 | -10 | hv | 1.2 | 10.4 | 10.4 | 10.4 | 0.28 | 0.35 | 0.32
63/25/38 MVA 110/20/10 kV | 0.89 | 35 | 0 | 0 | YN0yn0yn0 | 110 | 10 | 20 | 63 | 38 | 25 | 10 | 0 | -10 | hv | 1.2 | 10.4 | 10.4 | 10.4 | 0.28 | 0.35 | 0.32

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -71.9547 | -24.069
1 | 1 | 9.6687 | -163 | -14.4601
2 | 1 | 4.7711 | -85 | 3.649
3 | 0.98701 | -2.4066 | 0 | 0
4 | 0.97547 | -4.0173 | 90 | 30
5 | 1.0034 | 1.9256 | 0 | 0
6 | 0.98564 | 0.62154 | 100 | 35
7 | 0.99619 | 3.7991 | 0 | 0
8 | 0.95762 | -4.3499 | 125 | 50

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 71.9547 | 24.069 | -71.9547 | -20.753 | 0 | 3.3159 | 0.12697 | 0.12697 | 0.12697 | 1 | 0 | 0.98701 | -2.4066 | 30.3494
1 | 30.7283 | -0.58585 | -30.5547 | -13.688 | 0.17359 | -14.2738 | 0.05211 | 0.057438 | 0.057438 | 0.98701 | -2.4066 | 0.97547 | -4.0173 | 13.729
2 | -59.4453 | -16.312 | 60.8939 | -12.4275 | 1.4486 | -28.7395 | 0.10575 | 0.10366 | 0.10575 | 0.97547 | -4.0173 | 1.0034 | 1.9256 | 42.1285
3 | 85 | -3.649 | -85 | 7.8907 | 0 | 4.2417 | 0.14238 | 0.14238 | 0.14238 | 1 | 4.7711 | 1.0034 | 1.9256 | 28.3594
4 | 24.1061 | 4.5368 | -24.0106 | -24.4008 | 0.095486 | -19.864 | 0.040911 | 0.058123 | 0.058123 | 1.0034 | 1.9256 | 0.98564 | 0.62154 | 23.1545
5 | -75.9894 | -10.5992 | 76.4956 | 0.25624 | 0.50621 | -10.343 | 0.13027 | 0.1285 | 0.13027 | 0.98564 | 0.62154 | 0.99619 | 3.7991 | 31.137
6 | -163 | 2.2762 | 163 | 14.4601 | 0 | 16.7363 | 0.27385 | 0.27385 | 0.27385 | 0.99619 | 3.7991 | 1 | 9.6687 | 65.4561
7 | 86.5044 | -2.5324 | -84.0399 | -14.282 | 2.4645 | -16.8144 | 0.14538 | 0.14897 | 0.14897 | 0.99619 | 3.7991 | 0.95762 | -4.3499 | 35.6069
8 | -40.9601 | -35.718 | 41.2264 | 21.3389 | 0.26631 | -14.3791 | 0.094972 | 0.078708 | 0.094972 | 0.95762 | -4.3499 | 0.98701 | -2.4066 | 22.7005

## res_ext_grid
| p_mw | q_mvar
0 | 71.9547 | 24.069

## res_load
| p_mw | q_mvar
0 | 90 | 30
1 | 100 | 35
2 | 125 | 50

## res_gen
| p_mw | q_mvar | va_degree | vm_pu
0 | 163 | 14.4601 | 9.6687 | 1
1 | 85 | -3.649 | 4.7711 | 1

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | bus | max_vm_pu | float64
6 | bus | min_vm_pu | float64
7 | load | name | object
8 | load | bus | uint32
9 | load | p_mw | float64
10 | load | q_mvar | float64
11 | load | const_z_percent | float64
12 | load | const_i_percent | float64
13 | load | sn_mva | float64
14 | load | scaling | float64
15 | load | in_service | bool
16 | load | type | object
17 | load | controllable | bool
18 | gen | name | object
19 | gen | bus | uint32
20 | gen | p_mw | float64
21 | gen | vm_pu | float64
22 | gen | sn_mva | float64
23 | gen | min_q_mvar | float64
24 | gen | max_q_mvar | float64
25 | gen | scaling | float64
26 | gen | slack | bool
27 | gen | in_service | bool
28 | gen | slack_weight | float64
29 | gen | type | object
30 | gen | controllable | bool
31 | gen | max_p_mw | float64
32 | gen | min_p_mw | float64
33 | ext_grid | name | object
34 | ext_grid | bus | uint32
35 | ext_grid | vm_pu | float64
36 | ext_grid | va_degree | float64
37 | ext_grid | slack_weight | float64
38 | ext_grid | in_service | bool
39 | ext_grid | max_p_mw | float64
40 | ext_grid | min_p_mw | float64
41 | ext_grid | max_q_mvar | float64
42 | ext_grid | min_q_mvar | float64
43 | line | name | object
44 | line | std_type | object
45 | line | from_bus | uint32
46 | line | to_bus | uint32
47 | line | length_km | float64
48 | line | r_ohm_per_km | float64
49 | line | x_ohm_per_km | float64
50 | line | c_nf_per_km | float64
51 | line | g_us_per_km | float64
52 | line | max_i_ka | float64
53 | line | df | float64
54 | line | parallel | uint32
55 | line | type | object
56 | line | in_service | bool
57 | line | max_loading_percent | float64
58 | poly_cost | element | uint32
59 | poly_cost | et | object
60 | poly_cost | cp0_eur | float64
61 | poly_cost | cp1_eur_per_mw | float64
62 | poly_cost | cp2_eur_per_mw2 | float64
63 | poly_cost | cq0_eur | float64
64 | poly_cost | cq1_eur_per_mvar | float64
65 | poly_cost | cq2_eur_per_mvar2 | float64
66 | bus_geodata | x | float64
67 | bus_geodata | y | float64
68 | bus_geodata | coords | object
69 | res_bus | vm_pu | float64
70 | res_bus | va_degree | float64
71 | res_bus | p_mw | float64
72 | res_bus | q_mvar | float64
73 | res_line | p_from_mw | float64
74 | res_line | q_from_mvar | float64
75 | res_line | p_to_mw | float64
76 | res_line | q_to_mvar | float64
77 | res_line | pl_mw | float64
78 | res_line | ql_mvar | float64
79 | res_line | i_from_ka | float64
80 | res_line | i_to_ka | float64
81 | res_line | i_ka | float64
82 | res_line | vm_from_pu | float64
83 | res_line | va_from_degree | float64
84 | res_line | vm_to_pu | float64
85 | res_line | va_to_degree | float64
86 | res_line | loading_percent | float64
87 | res_ext_grid | p_mw | float64
88 | res_ext_grid | q_mvar | float64
89 | res_load | p_mw | float64
90 | res_load | q_mvar | float64
91 | res_gen | p_mw | float64
92 | res_gen | q_mvar | float64
93 | res_gen | va_degree | float64
94 | res_gen | vm_pu | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.10 | 2.14.0 | TRUE | FALSE |  | 60 | 100